## Inputs & Base Parameters
Thermal Lead Case |  |  | Electric Lead Case |  |  | Hybrid Thermal Lead Case
District Heating Parameters |  |  | District Heating Parameters |  |  | District Heating Parameters
Square Footage Included | 2000000 | sq ft | Square Footage Included | 2000000 | sq ft | Square Footage Included | 2000000 | sq ft
Peak Heat Input | 35 | Btu/hr-sq ft | Peak Heat Input | 35 | Btu/hr-sq ft | Peak Heat Input | 35 | Btu/hr-sq ft
Wood Fuel Heating Value | 4700 | Btu/lb, HHV | Wood Fuel Heating Value | 4700 | Btu/lb, HHV | Wood Fuel Heating Value | 4700 | Btu/lb, HHV
Economic Inputs |  |  | Economic Inputs |  |  | Economic Inputs
Fuel Cost | 35 | $/ton | Fuel Cost | 35 | $/ton | Wood Fuel Cost | 35 | $/ton
Elec. Sale | 0.09 | $/kWh | Elec. Sale | 0.09 | $/kWh | Oil Fuel Cost | 2 | $/gal
Elec. Purchases | 0.13 | $/kWh | Elec. Purchases | 0.13 | $/kWh | Elec. Sale | 0.09 | $/kWh
Thermal Sale | 16 | $/MMBtu | Thermal Sale | 16 | $/MMBtu | Elec. Purchases | 0.13 | $/kWh
Renewable Energy Credit | 0.035 | $/kWh | Renewable Energy Credit | 0.035 | $/kWh | Thermal Sale | 19 | $/MMBtu
[6 empty] | Renewable Energy Credit | 0.035 | $/kWh
Boiler Plant Metrics |  |  | Boiler Plant Metrics
Peak Heating Requirement | 70 | MMBtu/hr | Desired Electrical Output | 15 | MW | Boiler Plant Metrics
Design Boiler Capacity | 70000 | lb/hr | Design Boiler Capacity | 145800 | lb/hr | Peak Heating Requirement | 70 | MMBtu/hr
Turbine Throttle | 42000 | lb/hr | Turbine Throttle | 145800 | lb/hr | Wood-Fired Boiler Sizing Basis | 75% | % of Peak
|  |  | Minimum Electrical Output | 15 |  | Wood-Fired Boiler Capacity (Output) | 52.5 | MMBtu/hr
|  |  | Condensing Section Design Flow | 131220 | lb/hr | Design Boiler Capacity | 52500 | lb/hr
[6 empty] | Turbine Throttle | 39375 | lb/hr
Infrastructure Metrics |  |  | Infrastructure Metrics
Piping In Trench | 675 | $/ft | Piping In Trench | 675 | $/ft | Oil-Fired Boiler Sizing Basis | 50% | % of Peak
Linear Feet (plant to load pocket) | 2000 | ft | Linear Feet (plant to load pocket) | 10000 | ft | Oil-Fired Boiler Capacity (Output) | 35 | MMBtu/hr
Load Pocket Network Piping | 3000 | ft | Load Pocket Network Piping | 3000 | ft | Oil-Fired Boiler Capacity | 35000 | lb/hr
Piping Distribution Cost | 3375000 | $ | Piping Distribution Cost | 8775000 | $
Infrastructure Metrics
Manhole Unit Cost | 15000 | $/mh | Manhole Unit Cost | 15000 | $/mh | Piping In Trench | 675 | $/ft
Number of Manholes | 10 |  | Number of Manholes | 10 |  | Linear Feet (plant to load pocket) | 2000 | ft
Manhole Total Cost | 150000 |  | Manhole Total Cost | 150000 |  | Load Pocket Network Piping | 3000 | ft
[6 empty] | Piping Distribution Cost | 3375000 | $
Customer Connection Unit Cost | 35000 | $/cust | Customer Connection Unit Cost | 35000 | $/cust
Number of Connections | 50 |  | Number of Connections | 50 |  | Manhole Unit Cost | 15000 | $/mh
Interconnection Costs | 1750000 |  | Interconnection Costs | 1750000 |  | Number of Manholes | 10
[6 empty] | Manhole Total Cost | 150000
Total Infrastructure Cost | 5275000 |  | Total Infrastructure Cost | 10675000
[6 empty] | Customer Connection Unit Cost | 35000 | $/cust
[6 empty] | Number of Connections | 50
[6 empty] | Interconnection Costs | 1750000
[6 empty] | Total Infrastructure Cost | 5275000

## Thermal Lead
Option Description (e.g. Wood-Fired Boiler, Backpressure Steam Turbine, Thermal Lead, Boiler Sized for Heating Peak, Turbine Sized for 60% of Boiler Output)
Month | January | February | March | April | May | June | July | August | September | October | November | December | Totals
Hours in Month | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 8760
Steam Production (Mlb) | 27187.4644 | 26422.2825 | 25116.5743 | 18145.6495 | 6984.7802 | 6987.0895 | 5895.6454 | 5900.7587 | 6902.9673 | 15191.6413 | 20070.5629 | 24968.2883 | 189773.7041
District Heating Load Factor | 0.5317 | 0.5721 | 0.4912 | 0.3667 | 0.1366 | 0.1412 | 0.1153 | 0.1154 | 0.1395 | 0.2971 | 0.4056 | 0.4883
Steam to District (Mlb) | 25173.5782 | 24465.0764 | 23256.0873 | 16801.5273 | 6467.3891 | 6469.5273 | 5458.9309 | 5463.6655 | 6391.6364 | 14066.3345 | 18583.8545 | 23118.7855 | 175716.3927
Parasitic Steam (Mlb) | 2013.8863 | 1957.2061 | 1860.487 | 1344.1222 | 517.3911 | 517.5622 | 436.7145 | 437.0932 | 511.3309 | 1125.3068 | 1486.7084 | 1849.5028 | 14057.3114
Turbine Throttle Flow, % | 87.01% | 86.68% | 74.42% | 55.56% | 20.7% | 21.39% | 17.47% | 17.48% | 21.14% | 45.02% | 61.45% | 73.98%
Steam Rate, (lb/kWh) | 20.1661 | 20.1405 | 20.4215 | 25.6196 | 50.4328 | 49.7435 | 53.7277 | 53.7118 | 49.9973 | 31.0432 | 23.3749 | 20.4768
Electric Generation, Front End (MWh) | 1348.1756 | 1311.8993 | 1229.9102 | 708.2713 | 0 | 0 | 0 | 0 | 0 | 489.3704 | 858.6371 | 1219.3433 | 7165.6071
Gross Electric Generation (MWh) | 1348.1756 | 1311.8993 | 1229.9102 | 708.2713 | 0 | 0 | 0 | 0 | 0 | 489.3704 | 858.6371 | 1219.3433 | 7165.6071
Parasitic Power (MWh) | 221.5275 | 215.2927 | 204.6536 | 147.8534 | 56.913 | 56.9318 | 48.0386 | 48.0803 | 56.2464 | 123.7837 | 163.5379 | 203.4453 | 1546.3043
Net Generation - Sales (MWh) | 1126.6481 | 1096.6066 | 1025.2566 | 560.4179 | 0 | 0 | 0 | 0 | 0 | 365.5866 | 695.0992 | 1015.8979 | 5885.5129
Purchased Electricity - (MWh) | 0 | 0 | 0 | 0 | -56.913 | -56.9318 | -48.0386 | -48.0803 | -56.2464 | 0 | 0 | 0 | -266.2101
Fuel Input, tons/mo | 5134.9155 | 4990.3951 | 4743.7851 | 3427.1816 | 1319.2204 | 1319.6565 | 1113.5147 | 1114.4804 | 1303.7683 | 2869.256 | 3790.7413 | 4715.7782 | 35842.6931
Revenues
Electrical Sales | 101398.3257 | 98694.5969 | 92273.0937 | 50437.6078 | 0 | 0 | 0 | 0 | 0 | 32902.7984 | 62558.9272 | 91430.8145 | 529696.1642
Thermal Generation Revenue | 443054.976 | 430585.344 | 409307.136 | 295706.88 | 113826.048 | 113863.68 | 96077.184 | 96160.512 | 112492.8 | 247567.488 | 327075.84 | 406890.624 | 3092608.512
Renewable Energy Credits | 39432.6822 | 38381.2321 | 35883.9809 | 19614.6253 | 0 | 0 | 0 | 0 | 0 | 12795.5327 | 24328.4717 | 35556.4279 | 205992.9527
Total | 583885.9839 | 567661.173 | 537464.2105 | 365759.1131 | 113826.048 | 113863.68 | 96077.184 | 96160.512 | 112492.8 | 293265.8191 | 413963.239 | 533877.8664 | 3828297.6289
Fuel Costs
Fuel Costs | -179722.044 | -174663.828 | -166032.4769 | -119951.3554 | -46172.7124 | -46187.9776 | -38973.0142 | -39006.8156 | -45631.89 | -100423.9595 | -132675.947 | -165052.2363 | -1254494.257

## Electric Lead
Option Description (e.g. Wood-Fired Boiler, Condensing-Extracting Steam Turbine, Electric Lead, Extraction Based Upon District Heating Needs)
Month | January | February | March | April | May | June | July | August | September | October | November | December | Totals
Hours in Month | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 8760
Boiler Steam Generation (lb/hr) | 145800 | 145800 | 145800 | 145800 | 145800 | 145800 | 145800 | 145800 | 145800 | 145800 | 145800 | 145800 | 1749600
Steam Production (Mlb) | 108475.2 | 97977.6 | 108475.2 | 104976 | 108475.2 | 104976 | 108475.2 | 108475.2 | 104976 | 108475.2 | 104976 | 108475.2 | 1277208
District Heating Load Factor | 0.5317 | 0.5721 | 0.4912 | 0.3667 | 0.1366 | 0.1412 | 0.1153 | 0.1154 | 0.1395 | 0.2971 | 0.4056 | 0.4883
Steam to District (Mlb) | 25173.5782 | 24465.0764 | 23256.0873 | 16801.5273 | 6467.3891 | 6469.5273 | 5458.9309 | 5463.6655 | 6391.6364 | 14066.3345 | 18583.8545 | 23118.7855 | 175716.3927
Parasitic Steam (Mlb) | 8678.016 | 7838.208 | 8678.016 | 8398.08 | 8678.016 | 8398.08 | 8678.016 | 8678.016 | 8398.08 | 8678.016 | 8398.08 | 8678.016 | 102176.64
Steam to Condenser (Mlb) | 74623.6058 | 65674.3156 | 76541.0967 | 79776.3927 | 93329.7949 | 90108.3927 | 94338.2531 | 94333.5185 | 90186.2836 | 85730.8495 | 77994.0655 | 76678.3985 | 999314.9673
Steam Rate, Front End (lb/kWh) | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5
Electric Generation, Front End (MWh) | 5291.4732 | 4779.3951 | 5291.4732 | 5120.7805 | 5291.4732 | 5120.7805 | 5291.4732 | 5291.4732 | 5120.7805 | 5291.4732 | 5120.7805 | 5291.4732 | 62302.8293
Back-End Flow, % | 76.44% | 74.48% | 78.4% | 84.44% | 95.6% | 95.37% | 96.63% | 96.63% | 95.46% | 87.81% | 82.55% | 78.54%
Steam Rate, Condensing Section (lb/kWh) | 14.5891 | 14.7386 | 14.4845 | 14.4459 | 15.4993 | 15.4639 | 15.6706 | 15.6698 | 15.4769 | 14.6106 | 14.4121 | 14.4787
Electric Generation, Condensing End (MWh) | 5115.0079 | 4455.9407 | 5284.3489 | 5522.4187 | 6021.5554 | 5827.0056 | 6020.0786 | 6020.0966 | 5827.1445 | 5867.7319 | 5411.7184 | 5295.9338 | 66668.981
Gross Electric Generation (MWh) | 10406.4811 | 9235.3358 | 10575.8221 | 10643.1992 | 11313.0285 | 10947.7861 | 11311.5517 | 11311.5698 | 10947.9249 | 11159.2051 | 10532.4989 | 10587.407 | 128971.8102
Parasitic Power (MWh) | 1144.7129 | 1015.8869 | 1163.3404 | 1170.7519 | 1244.4331 | 1204.2565 | 1244.2707 | 1244.2727 | 1204.2717 | 1227.5126 | 1158.5749 | 1164.6148 | 14186.8991
Net Generation - Sales (MWh) | 9261.7682 | 8219.4489 | 9412.4816 | 9472.4473 | 10068.5954 | 9743.5296 | 10067.281 | 10067.2971 | 9743.6532 | 9931.6925 | 9373.924 | 9422.7922 | 114784.9111
Fuel Input, tons/mo | 20487.7874 | 18505.0983 | 20487.7874 | 19826.891 | 20487.7874 | 19826.891 | 20487.7874 | 20487.7874 | 19826.891 | 20487.7874 | 19826.891 | 20487.7874 | 241227.1738
Revenues
Electrical Sales | 833559.1355 | 739750.3973 | 847123.3466 | 852520.2562 | 906173.5867 | 876917.6656 | 906055.293 | 906056.7416 | 876928.7879 | 893852.329 | 843653.1598 | 848051.3018 | 10330642.0009
Thermal Generation Revenue | 443054.976 | 430585.344 | 409307.136 | 295706.88 | 113826.048 | 113863.68 | 96077.184 | 96160.512 | 112492.8 | 247567.488 | 327075.84 | 406890.624 | 3092608.512
Renewable Energy Credits | 324161.886 | 287680.71 | 329436.857 | 331535.6552 | 352400.8393 | 341023.5366 | 352354.8362 | 352355.3995 | 341027.862 | 347609.2391 | 328087.3399 | 329797.7285 | 4017471.8892
Total | 1600775.9975 | 1458016.4513 | 1585867.3396 | 1479762.7913 | 1372400.474 | 1331804.8822 | 1354487.3132 | 1354572.6531 | 1330449.4499 | 1489029.0561 | 1498816.3397 | 1584739.6543 | 17440722.4022
Fuel Costs
Fuel Costs | 717072.5578 | 647678.4393 | 717072.5578 | 693941.1849 | 717072.5578 | 693941.1849 | 717072.5578 | 717072.5578 | 693941.1849 | 717072.5578 | 693941.1849 | 717072.5578 | 8442951.0835

## Hybrid Thermal
Option Description (e.g. Wood-Fired Boiler, Backpressure Steam Turbine, Thermal Lead, Boiler Sized for Heating Peak, Turbine Sized for 60% of Boiler Output)
Month | January | February | March | April | May | June | July | August | September | October | November | December | Totals
Hours in Month | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 8760
District Heating Load Factor | 0.5317 | 0.5721 | 0.4912 | 0.3667 | 0.1366 | 0.1412 | 0.1153 | 0.1154 | 0.1395 | 0.2971 | 0.4056 | 0.4883 | 3.8007
Steam to District (Mlb) | 25173.5782 | 24465.0764 | 23256.0873 | 16801.5273 | 6467.3891 | 6469.5273 | 5458.9309 | 5463.6655 | 6391.6364 | 14066.3345 | 18583.8545 | 23118.7855 | 175716.3927
Parasitic Steam (Mlb) | 2013.8863 | 1957.2061 | 1860.487 | 1344.1222 | 517.3911 | 517.5622 | 436.7145 | 437.0932 | 511.3309 | 1125.3068 | 1486.7084 | 1849.5028 | 14057.3114
Steam Production (Mlb) | 27187.4644 | 26422.2825 | 25116.5743 | 18145.6495 | 6984.7802 | 6987.0895 | 5895.6454 | 5900.7587 | 6902.9673 | 15191.6413 | 20070.5629 | 24968.2883 | 189773.7041
Wood-Fired Load Factor | 80% | 75% | 85% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 85%
Wood-Fired Annual Duty Contribution | 0.42536 | 0.42907 | 0.41752 | 0.3667 | 0.1366 | 0.1412 | 0.1153 | 0.1154 | 0.1395 | 0.2971 | 0.4056 | 0.41506 | 3.4044 | 0.89573
Wood-Fired Steam Production (Mlb) | 21749.9715 | 19816.7119 | 21349.0881 | 18145.6495 | 6984.7802 | 6987.0895 | 5895.6454 | 5900.7587 | 6902.9673 | 15191.6413 | 20070.5629 | 21223.045
Turbine Throttle Flow, % | 74.24% | 74.89% | 72.88% | 64.01% | 23.84% | 24.65% | 20.13% | 20.14% | 24.35% | 51.86% | 70.8% | 72.45%
Steam Rate, (lb/kWh) | 20.4437 | 20.3659 | 20.6304 | 22.5782 | 47.3838 | 46.6313 | 51.0044 | 50.9869 | 46.9082 | 27.3185 | 20.9726 | 20.6954
Electric Generation, Front End (MWh) | 1329.8688 | 1297.3815 | 1217.4516 | 803.6816 | 0 | 0 | 0 | 0 | 0 | 556.0936 | 956.9893 | 1206.4631 | 7367.9295
Gross Electric Generation (MWh) | 1329.8688 | 1297.3815 | 1217.4516 | 803.6816 | 0 | 0 | 0 | 0 | 0 | 556.0936 | 956.9893 | 1206.4631 | 7367.9295
Parasitic Power (MWh) | 221.5275 | 215.2927 | 204.6536 | 147.8534 | 56.913 | 56.9318 | 48.0386 | 48.0803 | 56.2464 | 123.7837 | 163.5379 | 203.4453 | 1546.3043
Net Generation - Sales (MWh) | 1108.3413 | 1082.0889 | 1012.798 | 655.8281 | 0 | 0 | 0 | 0 | 0 | 432.3099 | 793.4513 | 1003.0178 | 6087.8354
Purchased Electricity - (MWh) | 0 | 0 | 0 | 0 | -56.913 | -56.9318 | -48.0386 | -48.0803 | -56.2464 | 0 | 0 | 0 | -266.2101
Wood Fuel Input, tons/mo | 4107.9324 | 3742.7963 | 4032.2173 | 3427.1816 | 1319.2204 | 1319.6565 | 1113.5147 | 1114.4804 | 1303.7683 | 2869.256 | 3790.7413 | 4008.4115 | 32149.1767
Oil Fuel Input, gal/mo | 45696.8517 | 55513.4116 | 31662.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31475.1354 | 164347.4641
Revenues
Electrical Sales | 99750.7171 | 97387.9973 | 91151.8236 | 59024.5313 | 0 | 0 | 0 | 0 | 0 | 38907.8895 | 71410.6206 | 90271.6023 | 547905.1817
Thermal Generation Revenue | 443054.976 | 430585.344 | 409307.136 | 295706.88 | 113826.048 | 113863.68 | 96077.184 | 96160.512 | 112492.8 | 247567.488 | 327075.84 | 406890.624 | 3092608.512
Renewable Energy Credits | 38791.9455 | 37873.1101 | 35447.9314 | 22953.9844 | 0 | 0 | 0 | 0 | 0 | 15130.8459 | 27770.7969 | 35105.6231 | 213074.2373
Total | 581597.6386 | 565846.4514 | 535906.891 | 377685.3957 | 113826.048 | 113863.68 | 96077.184 | 96160.512 | 112492.8 | 301606.2235 | 426257.2575 | 532267.8494 | 3853587.9311
Fuel Costs
Fuel Costs | -235171.3385 | -242024.6942 | -204451.7361 | -119951.3554 | -46172.7124 | -46187.9776 | -38973.0142 | -39006.8156 | -45631.89 | -100423.9595 | -132675.947 | -203244.6717 | -1453916.1124

## Typical Oil Customer
Customer Site Heating Parameters
Square Footage Included | 50000 | sq ft
Peak Heat Input | 35 | Btu/hr-sq ft
District Energy Cost | 19 | $/MMBtu
Heating Oil Heating Value | 138000 | Btu/gal*
Heating Oil Cost | 2.4 | $/gal
Heating Oil Cost (LHV Basis) | 18.4348 | $/MMBtu
Month | January | February | March | April | May | June | July | August | September | October | November | December | Totals
Hours in Month | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 8760
Heating Load Factor | 0.5317 | 0.5721 | 0.4912 | 0.3667 | 0.1366 | 0.1412 | 0.1153 | 0.1154 | 0.1395 | 0.2971 | 0.4056 | 0.4883
Heating Demand, MMBtu | 692.2734 | 672.7896 | 639.5424 | 462.042 | 177.8532 | 177.912 | 150.1206 | 150.2508 | 175.77 | 386.8242 | 511.056 | 635.7666 | 4832.2008
Boiler Efficiency, LHV | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Oil Purchased, gallons | 5908.2915 | 5742.0046 | 5458.2524 | 3943.3536 | 1517.9098 | 1518.4116 | 1281.2225 | 1282.3337 | 1500.1304 | 3301.3982 | 4361.6696 | 5426.0273 | 41241.0052
Purchased Oil Cost, $ | 14179.8996 | 13780.8111 | 13099.8057 | 9464.0487 | 3642.9834 | 3644.1878 | 3074.934 | 3077.6009 | 3600.313 | 7923.3556 | 10468.007 | 13022.4656 | 98978.4125
District Energy Cost | 13153.1946 | 12783.0024 | 12151.3056 | 8778.798 | 3379.2108 | 3380.328 | 2852.2914 | 2854.7652 | 3339.63 | 7349.6598 | 9710.064 | 12079.5654 | 91811.8152
0.92759

## Executive Summary
|  |  | Condensing Turbine w/extraction | Back Pressure Turbine | Hybrid Thermal w/Backpressure Turbine
|  |  | Electric Lead | Thermal Lead | Thermal Lead
District Energy Metrics
| Square Footage Heated |  | 2000000 | 2000000 | 2000000
Biomass Plant Ratings
| Steam Turbine Output | MW | 15 | 2.0488 | 1.9207
| Wood-Fired Boiler Capacity | lb/hr | 145800 | 70000 | 52500
| Oil-Fired Boiler Capacity | lb/hr |  |  | 35000
Power Generation
| Electric Value (REC + Grid Sales) | $/(kWh) | 0.125 | 0.125 | 0.125
| Electric Sales | kWh | 114784911.1213 | 5885512.9356 | 6087835.3525
| Electric Sales Revenue | $ | 14348113.8902 | 735689.1169 | 760979.4191
Thermal Generation
| Heat Value | $/MMBtu | 16 | 16 | 19
| Thermal Sales | MMBtu | 193288.032 | 193288.032 | 193288.032
| Thermal Sales | $ | 3092608.512 | 3092608.512 | 3672472.608
Wood Fuel Consumption
| Wood Fuel Unit Cost | $/ton | 35 | 35 | 35
| Annual Consumption | ton/yr | 241227.1738 | 35842.6931 | 32149.1767
| Annual Consumption | MMBtu/yr | 2267535.4338 | 336921.3147 | 302202.2609
| Wood Fuel Annual Cost | $/yr | 8442951.0835 | 1254494.257 | 1125221.1842
Oil Fuel Consumption
| Oil Fuel Unit Cost | $/gal |  |  | 2
| Annual Consumption | gal/yr |  |  | 164347.4641
| Oil Fuel Annual Cost | $/yr |  |  | 328694.9282
Add'l Operating Expenses
| Total | $ | 4148181.4831 | 1871600.5211 | 850000
Net Revenue |  | $ | 4849589.8356 | 702202.8508 | 2129535.9147
Plant Capital Cost
| Budgetary Capital | $/kW | 4000 | 2700 | 2700 | Note: The $2,700/kW for the thermal lead case is applied to an equivalent boiler production
| EPC Cost |  | 60000000 | 21000000 | 15750000 | to estimate the EPC cost. For instance, a boiler production of 70,000 lb/hr equates to roughly
| ProjectTotal | $ | 78000000 | 27300000 | 18900000 | 7,800 kW of generation, and $2,700 * 7,800 = $23,333,333.
Distribution Infrastructure Cost |  |  | 10675000 | 5275000 | 5275000
Simplified Financial Analysis
| Total Installation Capital |  | 88675000 | 32575000 | 24175000
| Desired Capital Recovery | % | 15% | 15% | 5%
| Capital Recovery Period | yrs | 25 | 25 | 25
| Capital Recovery Payment |  | -13717969.5007 | -5039333.0306 | -1715275.6552
EPC = Engineer, Procure, Construct